## XARJTAGRICXVA
Cost Estimation
Zestafoni-Kutaisi By-pass Highway, Road Lighting Network of km0+000-km15+172 Road Section
N | Work Description | Unit | Quantity | Unit Cost, GEL | Total Cost, GEL
1 | 2 | 3 | 4 | 5 | 6
Chapter 1. Installation of 10 kV Branch Lines and Metering Units
1 | Installation of reinforced concrete post for 10 kV overhead line (see Dwg. N4e) | It | 6
2 | Installation of three-pole РЛДН 3-1-10/200 type (or similar) line disconnector with manual actuator | It | 3
3 | Installation of ОПН-10 type (or similar) overvoltage limiter | It | 9
4 | Digging of trench (depth - 0.8m, width - 0.6m) in III category ground with use of mechanisms, piling of dug soil next to trench | m3 | 30
5 | Digging of trench (depth - 0.6m, width - 0.6m) in III category ground with use of mechanisms, piling of dug soil next to trench | m3 | 18
6 | Making of reinforced concrete foundation and socle with use of encasement forms | m3 | 8
7 | Back-filling of dug soil and leveling of sand-gravel mix by hand | m3 | 70
8 | Connection of AC-50 type conductors | It | 9
9 | Connection of ВВГ-10 type (or similar) 3x50mm2 cable to clamps and fixing on reinforced concrete post with brackets | m | 24
10 | Installation of ВВГ-10 type (or similar) 3X50mm2 cable in trench and connection to clamps of metering unit | m | 36
11 | Installation of vertical electrodes of grounding circuit made of steel angle bar | m | 16
12 | Installation of horizontal grounding circuit made of steel strips | m | 90
13 | Installation of one-cubicle 10kV voltage metering unit and setting the equipment | Set | 1
14 | Installation of two-cubicle 10kV voltage metering unit and setting the equipment | Set | 2
Total, Chapter 1.
Chapter 2. Installation of 10/0.4 kV and 6/0.4kV voltage 25 kVA power capacity transformer substations
1 | Digging of trench (depth - 0.6m, width - 0.6m) for foundation in III category ground with use of mechanisms, piling of dug soil next to trench | m3 | 48
2 | Digging of trench (depth - 0.6m, width - 0.4m) for grounding circuit in III category ground with use of mechanisms, piling of dug soil next to trench | m3 | 69
3 | Installation of sand-gravel mix layer under the foundation of metering units | m3 | 133
4 | Making of gravel layer under the foundation of metering units | m3 | 22
5 | Installation of metering units with use of concrete, class B 15 | m3 | 107
6 | Back-filling of dug soil | m3 | 117
7 | Installation of fence of substations (size 6.0x7.0, height 2.0m) with use of metal mesh (cell size 50x50mm) | m | 286
Installation works
1 | Installation of vertical grounding circuit made of metal (steel angle bar 40x40 mm, length 2m) at the bottom of trench | m | 264
2 | Installation/welding of horizontal grounding circuit made of steel strips (40x4mm) and connection with packaged transformer substations | m | 352
3 | Installation of packaged transformer substations on foundation and welding with elements, including:
3.1 | with two 10kV voltage cubicles and two 0.4kV outgoing lines | Set | 5
3.2 | with two 10kV voltage cubicles and three 0.4kV outgoing lines | Set | 1
3.3 | with three 10kV voltage cubicles and two 0.4kV outgoing lines | Set | 2
3.4 | with three 10kV voltage cubicles and three 0.4kV outgoing lines | Set | 1
3.5 | with three 10kV voltage cubicles and four 0.4kV outgoing lines | Set | 1
3.6 | with four 10kV voltage cubicles and four 0.4kV outgoing lines | Set | 1
Total, Chapter 2.
Chapter 3. Installation of 10kV voltage feeding and distribution network
1 | Digging of cable trench (depth - 0.8m, width - 0.6m) with use of mechanisms, piling of dug soil next to trench (in road dividing line between substations: N1-N4, N5-N8, N9-N11) | m3 | 5280
2 | Digging of cable trench (depth - 1.0m, width - 0.6m) in III category ground with use of mechanisms, piling of dug soil next to trench (from metering units and transformer substations to road edge) | m3 | 680
3 | Digging of pits (size 2.0m(H)X1.5m(L)X1.5m(W)) in III category ground with use of mechanisms for communication pits, piling of dug soil next to pits | m3 | 37
4 | Installation of assembled reinforce concrete communication pits (d-1000mm). Making of hole in cover plate (thick 0.3m) of reinforce concrete drainage tube under the road. | It | 7
5 | Installation of 3X50 mm2 cross section 10kV copper cables in d=75mm protective PVC pipes and installation in existing reinforce concrete pipes with use of brackets | m | 175
6 | Installation of 3X50 mm2 cross section 10kV copper cables in Æ75mm protective PVC pipes and installation on bridge structures by hungers | m | 50
7 | Installation of 3X50 mm2 cross section 10kV copper cables in structures of 10/0.4kV substations | m | 25
8 | Installation of 3X50 mm2 cross section 10kV copper cables in trench on road dividing line | m | 3150
9 | Installation of 3X50 mm2 cross section 10kV copper cables in communication pit | m | 8
10 | Installation of 3X50 mm2 cross section 10kV copper cables in trench, from metering units to road edge | m | 760
11 | Installation of 3X35 mm2 cross section 10kV copper cables in d=75mm protective PVC pipes and installation in existing reinforce concrete pipes with use of brackets | m | 95
12 | Installation of 3X35mm2 cross section 10kV copper cables in Æ75mm protective PVC pipes and installation on bridge structures by hungers | m | 170
13 | Installation of 3X35mm2 cross section 10/0.4kV copper cables on structures of substations | m | 60
14 | Installation of 3X35 mm2 cross section 10kV copper cables in trench on road dividing line | m | 8090
15 | Installation of 3X35 mm2 cross section 10kV copper cables in communication pit | m | 24
16 | Installation of 3X35 mm2 cross section 10kV copper cables in trench from substations to road edge | m | 430
17 | Installation of joining couplings for 3X50 mm2 cross section copper cables | Set | 15
18 | Installation of joining couplings for 3X35 mm2 cross section copper cables | Set | 27
19 | Installation of terminal couplings for 3X50 mm2 cross section 10kV copper cables | Set | 10
20 | Installation of terminal couplings for 3X35 mm2 cross section 10kV copper cables | Set | 12
Total, Chapter 3.
Chapter 4. Installation of 0.4kV Road Lighting Network, Lighting Posts and Fixtures
1 | Digging of cable trench (depth-0.6m, width-0.4m) in III category ground, piling of dug soil next to trench III | m3 | 1050
2 | Digging of cable trench (depth-0.8m, width-0.6m) in III category ground with use of mechanisms, piling of dug soil next to trench III | m3 | 2016
3 | Digging of pits (size 1.5(H)X1.5(L)X1.5(W)m) in III category ground with use of mechanisms for installation of A2 type lighting posts, piling of dug soil next to pits | m3 | 1220
4 | Drilling of pits (depth 2.5m) in IV category ground with use of Æ520mm steep reinforcement pipes for installation of A type and D type lighting posts, piling of dug soil next to pits | m | 243
5 | Backfilling of cable trenches and installation of warning tape after backfilling of 20cm thick layer of soil | m3 | 9020
6 | Backfilling of foundation pits | m3 | 890
7 | Installation of mounting joints for B type and C type lighting posts on bridges and overpasses (see Dwg.N 63) | It | 50
8 | Installation of cable hungers on structures of bridges and overpasses (see Dwg. N 59) | Set | 1030
9 | Making of reinforced concrete foundation for A2 type lighting posts (see Dwg. N 59) | It | 356
10 | Installation of piles for D type lighting posts (see Dwg. N 63) | It | 97
11 | Installation of A2 type lighting posts with use of flange joints on reinforced concrete foundations (see Dwg. N 57, 59) | It | 356
12 | Installation of B type and C type lighting posts with use of flange joints on bridges and overpasses (see Dwg. N 57, 61) | It | 50
13 | Installation of D type lighting post with use of flage joint on drilled reinforced concrete piles (see Dwg. N 57, 63) | It | 97
14 | Installation of 4X16 mm2 cross section cable in Æ40mm protective PVC pipes and installation on the top of drainage tube under the road, with use of brackets (see Dwg. N 56) | m | 560
15 | Installation of 4X16 mm2 cross section cable in Æ40mm corrugated protective PVC pipes and installation on hungers fixed on bridge (see dwg. N 56) | m | 1030
16 | Installation of 4X16 mm2 cross section cable in Æ40mm corrugated protective PVC pipes and installation under bridge with use of brackets on reinforce concrete structures | m | 224
17 | Installation of 4X16 mm2 cross section cable in Æ40mm protective corrugated protective PVC pipes and installation vertically on reinforce concrete body of bridge with use of brackets | m | 6
18 | Installation of 4X16 mm2 cross section cable in trench | m | 8570
19 | Installation of 4X16 mm2 cross section cable in communication pit | m | 14
20 | Installation of 4X16 mm2 cross section cable in 10/0.4kV voltage transformer substations | m | 135
21 | Cleaning of ends of 4X16 mm2 cross section 0.4kV voltage copper cable and connection to clamps inside lighting posts | Ends | 4024
22 | Pulling of 3X1.5 mm2 cross section 0.23 kV voltage copper cables through lighting post body and lighting fixture bracket | m | 7250
23 | Cleaning of ends of 3X1.5 mm2 cross section copper cable and connection to clamps in lighting post, lighting fixture, grounding clamp and fuse (see dwg. N 57) | Ends | 5092
24 | Installation of 3X1.5 mm2 cross section 0.23 kV voltage copper cable in Æ20 mm2 corrugated protective PVC pipes and installation on strained rope between bridges, with use of brackets (see Dwg. N 56) | m | 60
25 | Installation of two-arm brackets and one lighting fixture on A type lighting post | It | 712
26 | Installation of one-art brackets and one lighting fixture on B type, C type and D type lighting posts | It | 147
27 | Installation of o.4kV vertical grounding electrodes and grounding circuit (steel angle bars and steel strips, depth - 2.0m ) and connection to steel plates undet lighting posts | Set | 37
28 | Installation of clamp boxes inside lighting posts | It | 503
29 | Installation of outdoor distribution boxes | It | 11
Total, Chapter 4.
Sum of chapters 1-4
VAT - 18%
Total Cost
*unforseen expenses - 5%
Total cost with the accrued interests
*) The mentioned funds shall be applied only by permission and on the initiative of the Employer (Purchaser), or after the Employer (Purchaser) shall review, approve and take relevant decision on reasonable and substantiated proposal of the Supplier