## Sheet1
# | Technical specifications | Unit of | Required technical specification | Offered technical specification
1 |  | 3 | 4 | 5
1 | Gas insulated circuit braker (with 3 drives), with steel support structure, anchor, fixing bolts and apparatus clamps
1.1 | standard |  | IEC 62271-100
or analogous
1.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
1.3 | maximum ice thickness | mm | ≥20
(forth zone)
1.4 | maximum wind speed | m/sec | ≥20
(second zone)
1.5 | maximum air temperature | °C | ≥ +40
1.6 | minimum air temperature | °C | ≤ -30
technical specifications
1.7 | installation type |  | Outdoor instalation
1.8 | altitude above sea level | mtr. | > 1000
1.9 | control regime |  | single-pole
operation
1.1 | nominal voltage | kw | 110
1.11 | maximum permitted voltage | kw | ≥123
1.12 | arc extinguishing area |  | SF6
1.13 | nominal frequency | Hz | 50
1.14 | industrial frequency testing voltage | kw | ≥230
1.15 | lightning impulse testing voltage | kw | ≥550
1.16 | number of disconnecting spools | Pc. | 2 (Two)
1.17 | nominal current | A | ≥1250
1.18 | leakage way nominal distance | mm/kw | ≥25
1.19 | thermal stability current | ka | ≥20
1.2 | maximum dynamic stability current | ka | ≥50
1.21 | full time of switch-off | mk/sec | ≤ 50
1.22 | length of short circuit | sec | ≥3
1.23 | nominal cycles of operations |  | O-0,3s-CO-3m-CO
1.24 | number of drive shafts |  | 3
1.25 | insulation material |  | porcelain
1.26 | distance between the phases | mm | 1700-2000
1.27 | supporting construction height | mm | 2400-2700
1.28 | driving voltage | v | 220 DC
1.29 | drive shafts' feeding voltage | v | 220 DC
1.3 | heater's feeding voltage | v | 220 AC
1.31 | number of interruptions on the pole |  | one
1.32 | circuit braker clips for AC-240/39 type wire | Pc. | 6
2 | one earthening three-pole disconnector with steel support structure, anchor, fixing bolts and apparatus clamps
2.1 | standard |  | IEC 62271-102
or analogous
2.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
2.3 | maximum ice thickness | mm | ≥20
(forth zone)
2.4 | maximum wind speed | m/sec | ≥20
(second zone)
2.5 | maximum air temperature | °C | ≥ +40
2.6 | minimum air temperature | °C | ≤ -30
technical specifications
2.7 | installation type |  | Outdoor instalation
2.8 | altitude above sea level | mtr. | > 1000
2.9 | control type |  | remote and local control
2.1 | drive shaft type |  | el. motor drive
2.11 | earthing blade with remote and local control |  | one
2.12 | nominal voltage | kw | 110
2.13 | maximum permitted voltage | kw | ≥ 123
2.14 | nominal frequency | Hz | 50
2.15 | nominal current | A | ≥ 1600
2.16 | thermal stability current | ka | ≥ 20
2.17 | maximum dynamic stability current | ka | ≥ 50
2.18 | switch on/off | sec | ≤ 10
2.19 | length of short circuit | sec | ≥1
2.2 | control regime |  | three-pole
2.21 | distance between the phases | mm | 2000
2.22 | supporting construction height | mm | 2400-2700
2.23 | driving voltage | v | 220 DC
2.24 | drive shafts' feeding voltage | v | 220 DC
2.25 | heater's feeding voltage | v | 220 AC
2.26 | insulation material |  | porcelain
2.27 | leakage way nominal distance | mm/kw | ≥25
2.28 | free block-controls driven to the clips in the drive shaft chamber |  | Yes
2.29 | disconnector's clips for AC-240/39 type wire | Pc. | 6
3 | Two earthening three-pole disconnector with steel support structure, anchor, fixing bolts and apparatus clamps
3.1 | standard |  | IEC 62271-102
or analogous
3.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
3.3 | maximum ice thickness | mm | ≥20
(forth zone)
3.4 | maximum wind speed | m/sec | ≥20
(second zone)
3.5 | maximum air temperature | °C | ≥ +40
3.6 | minimum air temperature | °C | ≤ -30
technical specifications
3.7 | installation type |  | Outdoor instalation
3.8 | altitude above sea level | mtr. | > 1000
3.9 | control type |  | remote and local control
3.1 | drive shaft type |  | el. motor drive
3.11 | earthing blade with remote and local control |  | Two
3.12 | nominal voltage | kw | 110
3.13 | maximum operating voltage | kw | ≥ 123
3.14 | nominal frequency | Hz | 50
3.15 | nominal current | A | ≥ 1600
3.16 | thermal stability current | ka | ≥ 20
3.17 | maximum dynamic stability current | ka | ≥ 50
3.18 | switch on/off | sec | ≤ 10
3.19 | length of short circuit | sec | ≥1
3.2 | control regime |  | three-pole
3.21 | distance between the phases | mm | 2000
3.22 | supporting construction height | mm | 2400-2700
3.23 | driving voltage | v | 220 DC
3.24 | drive shafts' feeding voltage | v | 220 DC
3.25 | heater's feeding voltage | v | 220 AC
3.26 | insulation material |  | porcelain
3.27 | leakage way nominal distance | mm/kw | ≥25
3.28 | free block-controls driven to the clips in the drive shaft chamber |  | Yes
3.29 | disconnector clips for AC-400/51 type wire | Pc. | 6
4 | Surge arrestor with counter, with steel support structure, isolator and fixing bolts, with apparatus clamps.
4.1 | standard |  | IEC 60099-4
or analogous
4.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
4.3 | maximum ice thickness | mm | ≥20
(forth zone)
4.4 | maximum wind speed | m/sec | ≥20
(second zone)
4.5 | maximum air temperature | °C | ≥ +40
4.6 | minimum air temperature | °C | ≤ -30
technical specifications
4.7 | installation type |  | Outdoor instalation
4.8 | altitude above sea level | mtr. | > 1000
4.9 | nominal voltageUr | kw | 108
4.1 | lastingly permitted voltage Uc | kw | ≥ 86
4.11 | nominal frequency | Hz | 50
voltage permitted values for period of time
4.12 | 10 sec | kw | ≥ 117
4.13 | 1 sec | kw | ≥ 124
4.14 | residual voltage 0,5 ka at the time of impulse current and a 30/70 mcsec wave front | kw | ≥ 214
4.15 | residual voltage Imax= 0,5 ka at the time of impulse current and a 8/20 mcsec wave front | kw | ≥ 246
4.16 | leakage way nominal distance | mm/kw | ≥ 25
4.17 | registrar with a mechanical face |  | Yes
4.18 | Surge arrestor clips for AC-400/51 type wire | Pc. | 12
4.19 | supporting construction height | mm | 2400-2600
5 | Hybrid gas insulated circuit breaker with steel support structure, anchor, fixing bolts and apparatus clamps
5.1 | standard |  | IEC 62271-205
or analogous
5.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
5.3 | maximum ice thickness | mm | ≥20
(forth zone)
5.4 | maximum wind speed | m/sec | ≥20
(second zone)
5.5 | maximum air temperature | °C | ≥ +40
5.6 | minimum air temperature | °C | ≤ -30
5.7 | Seismic Scale |  | ≥ 9
technical specifications
5.8 | installation type |  | Outdoor instalation
5.9 | altitude above sea level | mtr. | > 1000
5.1 | control regime |  | single-pole
operation
5.11 | At the time emergency outage of circuit breaker, OHL side must not automatically earthing |  | yes
5.12 | nominal voltage | kw | 110
5.13 | maximum permitted voltage | kw | ≥123
5.14 | arc extinguishing area |  | SF6
5.15 | nominal frequency | Hz | 50
5.16 | industrial frequency testing voltage | kw | ≥230
5.17 | lightning impulse testing voltage | kw | ≥550
5.18 | number of disconnecting spools | Pc. | 2 (Two)
5.19 | nominal current | A | ≥1250
5.2 | leakage way nominal distance | mm/kw | ≥25
5.21 | thermal stability current | ka | ≥20
5.22 | maximum dynamic stability current | ka | ≥50
5.23 | full time of switch-off | mk.Sec | ≤ 50
5.24 | length of short circuit | sec | ≥3
5.25 | nominal cycles of operations |  | O-0,3s-CO-3m-CO
5.26 | Mechanical resource of operation |  | ≥10000
5.27 | number of drive shafts |  | 3
5.28 | insulation material |  | porcelain
5.29 | supporting construction height | mm | 2400-2700
5.3 | driving voltage | v | 220 DC
5.31 | drive shafts' feeding voltage | v | 220 DC
5.32 | heater's feeding voltage | v | 220 AC
5.33 | circuit breaker clips for AC-400/51 type wire | Pc. | 6
The hybrid gas-insulated breaker tank should not be welded and in the tank should be
5.34 | disconnector with one earthing blade |  | Please see chart
5,34,1 | standard |  | IEC 62271-102
or analogous
5,34,2 | nominal current | A | ≥1250
5,34,3 | length of short circuit | sec | ≥3
5,34,4 | industrial frequency testing voltage | kw | ≥230
5,34,5 | lightning impulse testing voltage | kw | ≥550
5,34,6 | driving voltage | v | 220 DC
5,34,7 | drive shafts' feeding voltage | v | 220 DC
5,34,8 | heater's feeding voltage | v | 220 AC
5.35 | current transformer |  | Please see chart
5,35,1 | standard |  | IEC 61869
or analogous
5,35,2 | nominal primary current | A | 800/400
5,35,3 | nominal secondary current | A | 5
5,35,4 | number of secondary rolls |  | 4
precision classes and capacities of the secondary rolls
5,35,5 | roll-1, coefficient 800/5, precision class and capacity0,5S – 25VA |  | roll is sealed
5,35,6 | roll-1, coefficient 400/5, precision class and capacity0,5S – 25VA |  | roll is sealed
5,35,7 | roll-2, 3 and 4 coefficient 800/5, precision class and capacity10P20 - 50VA
5,35,8 | roll-2, 3 and 4 coefficient 400/5, precision class and capacity10P20 - 50VA
5,35,9 | Change of the coefficients of the current transformers should be possible from the secondary roll |  | Yes
5.36 | voltage transformer |  | Please see chart
5,36,1 | standard |  | IEC 61869
or analogous
5,36,2 | roll -1,registry, voltage, v -100/√3 precision class and capacity, VA - 0,5/10 |  | roll is sealed
5,36,3 | roll - 2, reley protection, voltage,
ვ -100/√3 precision class and
capacity VA - 3P/20
6 | Gas insulated circuit braker (with 3 drives), with steel support structures, anchor, fixing boolts and apparatus clamps
6.1 | standard |  | IEC 62271-100
or analogous
6.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
6.3 | maximum ice thickness | mm | ≥20
(forth zone)
6.4 | maximum wind speed | m/sec | ≥40
(fifth zone)
6.5 | maximum air temperature | °C | ≥ +40
6.6 | minimum air temperature | °C | ≤ -30
technical specifications
6.7 | installation type |  | Outdoor instalation
6.8 | altitude above sea level | mtr. | ≤ 1000
6.9 | control regime |  | single-pole
operation
6.1 | nominal voltage | kw | 110
6.11 | maximum permitted voltage | kw | ≥123
6.12 | arc extinguishing area |  | SF6
6.13 | nominal frequency | Hz | 50
6.14 | industrial frequency testing voltage | kw | ≥230
6.15 | lightning impulse testing voltage | kw | ≥550
6.16 | number of disconnecting spools | Pc. | 2 (Two)
6.17 | nominal current | A | ≥2000
6.18 | leakage way nominal distance | mm/kw | ≥25
6.19 | thermal stability current | ka | ≥40
6.2 | maximum dynamic stability current | ka | ≥100
6.21 | full time of switch-off | mk.Sec | ≤ 50
6.22 | length of short circuit | sec | ≥3
6.23 | nominal cycles of operations |  | O-0,3s-CO-3m-CO
6.24 | number of drive shafts |  | 3
6.25 | insulation material |  | porcelain
6.26 | distance between the phases | mm | 1700-2000
6.27 | supporting construction height | mm | 2400-2700
6.28 | driving voltage | v | 220 DC
6.29 | drive shafts' feeding voltage | v | 220 DC
6.3 | heater's feeding voltage | v | 220 AC
6.31 | number of interruptions on the pole |  | one
6.32 | circuit braker clips for AC-400/51 type wire | Pc. | 6
7 | One earthening three-pole disconnector with steel support structure, anchor, fixing bolts and apparatus clamps
7.1 | standard |  | IEC 62271-102
or analogous
7.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
7.3 | maximum ice thickness | mm | ≥20
(forth zone)
7.4 | maximum wind speed | m/sec | ≥40
(fifth zone)
7.5 | maximum air temperature | °C | ≥ +40
7.6 | minimum air temperature | °C | ≤ -30
technical specifications
7.7 | installation type |  | Outdoor instalation
7.8 | altitude above sea level | mtr. | ≤ 1000
7.9 | control type |  | remote and local control
7.1 | drive shaft type |  | el. motor drive
7.11 | earthing blade with remote and local control |  | one
7.12 | nominal voltage | kw | 110
7.13 | maximum permitted voltage | kw | ≥ 123
7.14 | nominal frequency | Hz | 50
7.15 | nominal current | A | ≥ 2000
7.16 | thermal stability current | ka | ≥ 40
7.17 | maximum dynamic stability current | ka | ≥ 100
7.18 | switch on/off | sec | ≤ 10
7.19 | length of short circuit | sec | ≥1
7.2 | control regime |  | three-pole
7.21 | distance between the phases | mm | 2000-2100
7.22 | supporting construction height | mm | 2400-2700
7.23 | driving voltage | v | 220 DC
7.24 | drive shafts' feeding voltage | v | 220 DC
7.25 | heater's feeding voltage | v | 220 AC
7.26 | insulation material |  | porcelain
7.27 | leakage way nominal distance | mm/kw | ≥25
7.28 | free block-controls driven to the clips in the drive shaft chamber |  | Yes
7.29 | disconnector clips for AC-400/51 type wire | Pc. | 42
8 | Diagonal three-pole Disconnector, with steel support structures and anchor, fixin bolts, with apparatus clamps.
8.1 | standard |  | IEC 62271-102
or analogous
8.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
8.3 | maximum ice thickness | mm | ≥20
(forth zone)
8.4 | maximum wind speed | m/sec | ≥40
(fifth zone)
8.5 | maximum air temperature | °C | ≥ +40
8.6 | minimum air temperature | °C | ≤ -30
technical specifications
8.7 | installation type |  | Outdoor instalation
8.8 | altitude above sea level | mtr. | ≤ 1000
8.9 | control type |  | remote and local control
8.1 | positioning |  | diagonal
8.11 | earthing blade |  | without
8.12 | nominal voltage | kw | 110
8.13 | maximum permitted voltage | kw | ≥ 123
8.14 | nominal frequency | Hz | 50
8.15 | nominal current | A | ≥ 2000
8.16 | thermal stability current | ka | ≥ 40
8.17 | maximum dynamic stability current | ka | ≥ 100
8.18 | switch on/off | sec | ≤ 10
8.19 | length of short circuit | sec | ≥1
8.2 | control regime |  | three-pole
8.21 | distance between the phases | mm | 2800/3000
8.22 | supporting construction height | mm | 2400-2700
8.23 | driving voltage | v | 220 DC
8.24 | drive shafts' feeding voltage | v | 220 DC
8.25 | heater's feeding voltage | v | 220 AC
8.26 | insulation material |  | porcelain
8.27 | leakage way nominal distance | mm/kw | ≥25
8.28 | free block-controls driven to the clips in the drive shaft chamber |  | Yes
8.29 | disconnector clips for AC-400/51 type wire | Pc. | 12
9 | Surge arrestor with counter, with steel support structure, isolator and fixing bolts, with apparatus clamps.
9.1 | standard |  | IEC 60099-4
or analogous
9.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
9.3 | maximum ice thickness | mm | ≥20
(forth zone)
9.4 | maximum wind speed | m/sec | ≥40
(fifth zone)
9.5 | maximum air temperature | °C | ≥ +40
9.6 | minimum air temperature | °C | ≤ -30
technical specifications
9.7 | installation type |  | Outdoor instalation
9.8 | altitude above sea level | mtr. | > 1000
9.9 | nominal voltageUr | kw | 108
9.1 | lastingly permitted voltage Uc | kw | ≥ 86
9.11 | nominal frequency | Hz | 50
voltage permitted values for period of time
9.12 | 10 sec | kw | ≥ 117
9.13 | 1 sec | kw | ≥ 124
9.14 | residual voltage 0,5 ka at the time of impulse current and a 30/70 mcsec wave front | kw | ≥ 214
9.15 | residual voltage Imax= 0,5 ka at the time of impulse current and a 8/20 mcsec wave front | kw | ≥ 246
9.16 | leakage way nominal distance | mm/kw | ≥ 25
9.17 | registrar with a mechanical face |  | Yes
9.18 | Surge arrestor clips for AC-400/51 type wire | Pc. | 9
9.19 | supporting construction height | mm | 2400-2600
10 | Supporting isolator with fixing nuts and bolts on steel structure, apparatus clamps.
10.1 | standard |  | IEC 60273
or analogous
10.2 | typical test |  | upon delivery of the device
climate conditions
10.3 | maximum ice thickness | mm | ≥20
(forth zone)
10.4 | maximum wind speed | m/sec | ≥40
(fifth zone)
10.5 | maximum air temperature | °C | ≥ +40
10.6 | minimum air temperature | °C | ≤ -30
technical specifications
10.7 | insulator type |  | porcelain
10.8 | installation type |  | Outdoor instalation
10.9 | altitude above sea level | mtr. | ≤ 1000
10.1 | nominal voltage | kw | 110
10.11 | maximum permitted voltage | kw | ≥ 123
10.12 | minimum mechanical destructive power on bending | kn | ≥6
10.13 | minimum torque destructive moment | knm | ≥4
10.14 | lightning impulse testing voltage | kw | ≥550
10.15 | industrial frequency testing voltage | kw | ≥230
10.16 | leakage way nominal length | mm | ≥ 2900
10.17 | leakage way nominal distance | mm/kw | ≥ 25
10.18 | supporting insulator clips | Pc. | 8
for AC-400/51 type wire
10.19 | supporting construction height | mm | 2400-2600
11 | One earthening three-pole disconnector with steel support structure, anchor, fixing bolts and apparatus clamps
11.1 | standard |  | IEC 62271-102
or analogous
11.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
11.3 | maximum ice thickness | mm | ≥20
(forth zone)
11.4 | maximum wind speed | m/sec | ≥40
(fifth zone)
11.5 | maximum air temperature | °C | ≥ +40
11.6 | minimum air temperature | °C | ≤ -30
technical specifications
11.7 | installation type |  | Outdoor instalation
11.8 | altitude above sea level | mtr. | ≤ 1000
11.9 | control type |  | remote and local control
11.1 | drive shaft type |  | el. motor drive
11.11 | earthing blade with remote and local control |  | one
11.12 | nominal voltage | kw | 220
11.13 | maximum permitted voltage | kw | ≥ 245
11.14 | nominal frequency | Hz | 50
11.15 | nominal current | A | ≥ 2000
11.16 | thermal stability current | ka | ≥ 40
11.17 | maximum dynamic stability current | ka | ≥ 100
11.18 | switch on/off | sec | ≤ 10
11.19 | length of short circuit | sec | ≥1
11.2 | control regime |  | three-pole
11.21 | distance between the phases | mm | 4000
11.22 | supporting construction height | mm | 2400-2700
11.23 | driving voltage | v | 220 DC
11.24 | drive shafts' feeding voltage | v | 220 DC
11.25 | heater's feeding voltage | v | 220 AC
11.26 | insulation material |  | porcelain
11.27 | leakage way nominal distance | mm/kw | ≥25
11.28 | free block-controls driven to the clips in the drive shaft chamber |  | Yes
11.29 | disconnector clips for AC-400/51 type wire | Pc. | 24
12 | Two earthening three-pole disconnector with steel support structure, anchor, fixing bolts and apparatus clamps
12.1 | standard |  | IEC 62271-102
or analogous
12.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
12.3 | maximum ice thickness | mm | ≥20
(forth zone)
12.4 | maximum wind speed | m/sec | ≥40
(fifth zone)
12.5 | maximum air temperature | °C | ≥ +40
12.6 | minimum air temperature | °C | ≤ -30
technical specifications
12.7 | installation type |  | Outdoor instalation
12.8 | altitude above sea level | mtr. | ≤ 1000
12.9 | control type |  | remote and local control
12.1 | drive shaft type |  | el. motor drive
12.11 | earthing blade with remote and local control |  | Two
12.12 | nominal voltage | kw | 220
12.13 | maximum permitted voltage | kw | ≥ 245
12.14 | nominal frequency | Hz | 50
12.15 | nominal current | A | ≥ 2000
12.16 | thermal stability current | ka | ≥ 40
12.17 | maximum dynamic stability current | ka | ≥ 100
12.18 | switch on/off | sec | ≤ 10
12.19 | length of short circuit | sec | ≥1
12.2 | control regime |  | three-pole
12.21 | distance between the phases | mm | 4000
12.22 | supporting construction height | mm | 2400-2700
12.23 | driving voltage | v | 220 DC
12.24 | drive shafts' feeding voltage | v | 220 DC
12.25 | heater's feeding voltage | v | 220 AC
12.26 | insulation material |  | porcelain
12.27 | leakage way nominal distance | mm/kw | ≥25
12.28 | free block-controls driven to the clips in the drive shaft chamber |  | Yes
12.29 | disconnector clips for AC-400/51 type wire | Pc. | 6
13 | Surge arrestor with counter, with steel support structure, isolator and fixing bolts, with apparatus clamps.
13.1 | standard |  | IEC 60099-4
or analogous
13.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
13.3 | maximum ice thickness | mm | ≥20
(forth zone)
13.4 | maximum wind speed | m/sec | ≥40
(fifth zone)
13.5 | maximum air temperature | °C | ≥ +40
13.6 | minimum air temperature | °C | ≤ -30
technical specifications
13.7 | installation type |  | Outdoor instalation
13.8 | altitude above sea level | mtr. | ≤ 1000
13.9 | nominal voltageUr | kw | 192
13.1 | lastingly permitted voltage Uc | kw | ≥ 154
13.11 | nominal frequency | Hz | 50
voltage permitted values for period of time
13.12 | 10 sec | kw | ≥ 207
13.13 | 1 sec | kw | ≥ 221
13.14 | residual voltage 0,5 ka at the time of impulse current and a 30/70 mcsec wave front | kw | ≥ 380
13.15 | residual voltage Imax= 0,5 ka at the time of impulse current and a 8/20 mcsec wave front | kw | ≥ 438
13.16 | leakage way nominal distance | mm/kw | ≥ 25
13.17 | registrar with a mechanical face |  | Yes
13.18 | Surge arrestor clips for AC-400/51 type wire | Pc. | 6
13.19 | supporting construction height | mm | 2400-2600
14 | Supporting isolator with Steel Support structure, fixing nuts and bolts on steel structure, apparatus clamps
14.1 | standard |  | IEC 60273
or analogous
14.2 | typical test |  | upon delivery of the device
climate conditions
14.3 | maximum ice thickness | mm | ≥20
(forth zone)
14.4 | maximum wind speed | m/sec | ≥40
(fifth zone)
14.5 | maximum air temperature | °C | ≥ +40
14.6 | minimum air temperature | °C | ≤ -30
technical specifications
14.7 | insulator type |  | porcelain
14.8 | installation type |  | Outdoor instalation
14.9 | altitude above sea level | mtr. | ≤ 1000
14.1 | nominal voltage | kw | 220
14.11 | maximum permitted voltage | kw | ≥ 245
14.12 | minimum mechanical destructive power on bending | kn | ≥6
14.13 | minimum torque destructive moment | knm | ≥4
14.14 | lightning impulse testing voltage | kw | ≥1050
14.15 | industrial frequency testing voltage | kw | ≥550
14.16 | leakage way nominal length | mm | ≥ 6000
14.17 | leakage way nominal distance | mm/kw | ≥ 25
14.18 | supporting insulator clips | Pc. | 6
for AC-400/51 type wire
14.19 | supporting construction height | mm | 2400-2600
15 | Gas insulated circuit braker (with 1 drive), with steel support structures, anchors, fixing bolts on steel structure, apparatus clamps
15.1 | standard |  | IEC 62271-100
or analogous
15.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
15.3 | maximum ice thickness | mm | ≥20
(forth zone)
15.4 | maximum wind speed | m/sec | ≥40
(fifth zone)
15.5 | maximum air temperature | °C | ≥ +40
15.6 | minimum air temperature | °C | ≤ -30
technical specifications
15.7 | installation type |  | Outdoor instalation
15.8 | altitude above sea level | mtr. | ≤ 1000
15.9 | control regime |  | three-pole
operation
15.1 | nominal voltage | kw | 110
15.11 | maximum permitted voltage | kw | ≥123
15.12 | arc extinguishing area |  | SF6
15.13 | nominal frequency | Hz | 50
15.14 | industrial frequency testing voltage | kw | ≥230
15.15 | lightning impulse testing voltage | kw | ≥550
15.16 | number of disconnecting spools | Pc. | 2 (Two)
15.17 | nominal current | A | ≥2000
15.18 | leakage way nominal distance | mm/kw | ≥25
15.19 | thermal stability current | ka | ≥40
15.2 | maximum dynamic stability current | ka | ≥100
15.21 | full time of switch-off | mk.Sec | ≤ 50
15.22 | length of short circuit | sec | ≥3
15.23 | nominal cycles of operations |  | O-0,3s-CO-3m-CO
15.24 | number of drive shafts |  | 1
15.25 | insulation material |  | porcelain
15.26 | distance between the phases | mm | 1700-2000
15.27 | supporting construction height | mm | 2400-2700
15.28 | driving voltage | v | 220 DC
15.29 | drive shafts' feeding voltage | v | 220 DC
15.3 | heater's feeding voltage | v | 220 AC
15.31 | number of interruptions on the pole |  | one
15.32 | circuit braker clips for AC-240/39 type wire | Pc. | 12
16 | Two earthening three-pole Disconnector with steel support structure and anchor fixing bolts and apparatus clamps.
16.1 | standard |  | IEC 62271-102
or analogous
16.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
16.3 | maximum ice thickness | mm | ≥20
(forth zone)
16.4 | maximum wind speed | m/sec | ≥40
(fifth zone)
16.5 | maximum air temperature | °C | ≥ +40
16.6 | minimum air temperature | °C | ≤ -30
technical specifications
16.7 | installation type |  | Outdoor instalation
16.8 | altitude above sea level | mtr. | ≤ 1000
16.9 | control type |  | remote and local control
16.1 | drive shaft type |  | el. motor drive
16.11 | earthing blade with remote and local control |  | Two
16.12 | nominal voltage | kw | 110
16.13 | maximum permitted voltage | kw | ≥ 123
16.14 | nominal frequency | Hz | 50
16.15 | nominal current | A | ≥ 2000
16.16 | thermal stability current | ka | ≥ 40
16.17 | maximum dynamic stability current | ka | ≥ 100
16.18 | switch on/off | sec | ≤ 10
16.19 | length of short circuit | sec | ≥1
16.2 | control regime |  | three-pole
16.21 | distance between the phases | mm | 2000-2100
16.22 | supporting construction height | mm | 2400-2700
16.23 | driving voltage | v | 220 DC
16.24 | drive shafts' feeding voltage | v | 220 DC
16.25 | heater's feeding voltage | v | 220 AC
16.26 | insulation material |  | porcelain
16.27 | leakage way nominal distance | mm/kw | ≥25
16.28 | free block-controls driven to the clips in the drive shaft chamber |  | Yes
16.29 | disconnector clips for AC-400/51 type wire | Pc. | 6
17 | Diagonal three-pole Disconnector with steel support structures and anchor, fixing bolts, apparatus clamps.
17.1 | standard |  | IEC 62271-102
or analogous
17.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
17.3 | maximum ice thickness | mm | ≥20
(forth zone)
17.4 | maximum wind speed | m/sec | ≥40
(fifth zone)
17.5 | maximum air temperature | °C | ≥ +40
17.6 | minimum air temperature | °C | ≤ -30
technical specifications
17.7 | installation type |  | Outdoor instalation
17.8 | altitude above sea level | mtr. | ≤ 1000
17.9 | control type |  | remote and local control
17.1 | positioning |  | diagonal
17.11 | earthing blade |  | without
17.12 | nominal voltage | kw | 220
17.13 | maximum permitted voltage | kw | ≥ 245
17.14 | nominal frequency | Hz | 50
17.15 | nominal current | A | ≥ 2000
17.16 | thermal stability current | ka | ≥ 40
17.17 | maximum dynamic stability current | ka | ≥ 100
17.18 | switch on/off | sec | ≤ 10
17.19 | length of short circuit | sec | ≥1
17.2 | control regime |  | three-pole
17.21 | distance between the phases | mm | 4000/4000
17.22 | supporting construction height | mm | 2400-2700
17.23 | driving voltage | v | 220 DC
17.24 | drive shafts' feeding voltage | v | 220 DC
17.25 | heater's feeding voltage | v | 220 AC
17.26 | insulation material |  | porcelain
17.27 | leakage way nominal distance | mm/kw | ≥25
17.28 | free block-controls driven to the clips in the drive shaft chamber |  | Yes
17.29 | disconnector clips for AC-400/51 type wire | Pc. | 6
18 | Gas insulated circuit braker (with 3 drive), with steel support structures, anchors, fixing bolts on steel structure, apparatus clamps
18.1 | standard |  | IEC 62271-100
or analogous
18.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
18.3 | maximum ice thickness | mm | ≥20
(forth zone)
18.4 | maximum wind speed | m/sec | ≥22
(second zone)
18.5 | maximum air temperature | °C | ≥ +40
18.6 | minimum air temperature | °C | ≤ -30
technical specifications
18.7 | installation type |  | Outdoor instalation
18.8 | altitude above sea level | mtr. | ≤ 1000
18.9 | control regime |  | single-pole
operation
18.1 | nominal voltage | kw | 220
18.11 | maximum permitted voltage | kw | ≥245
18.12 | arc extinguishing area |  | SF6
18.13 | nominal frequency | Hz | 50
18.14 | industrial frequency testing voltage | kw | ≥460
18.15 | lightning impulse testing voltage | kw | ≥1050
18.16 | number of disconnecting spools | Pc. | 2 (Two)
18.17 | nominal current | A | ≥3150
18.18 | leakage way nominal distance | mm/kw | ≥25
18.19 | thermal stability current | ka | ≥40
18.2 | maximum dynamic stability current | ka | ≥100
18.21 | full time of switch-off | mk.Sec | ≤ 65
18.22 | length of short circuit | sec | ≥3
18.23 | nominal cycles of operations |  | O-0,3s-CO-3m-CO
18.24 | number of drive shafts |  | 3
18.25 | insulation material |  | porcelain
18.26 | distance between the phases | mm | 3500-4000
18.27 | supporting construction height | mm | 2400-2700
18.28 | driving voltage | v | 220 DC
18.29 | drive shafts' feeding voltage | v | 220 DC
18.3 | heater's feeding voltage | v | 220 AC
18.31 | number of interruptions on the pole |  | one
18.32 | circuit braker clips for AC-400/51 type wire | Pc. | 6
19 | Gas insulated circuit braker (with 1 drive), with steel support structures, anchors, fixing bolts on steel structure, apparatus clamps
19.1 | standard |  | IEC 62271-100
or analogous
19.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
19.3 | maximum ice thickness | mm | ≥20
(forth zone)
19.4 | maximum wind speed | m/sec | ≥22
(second zone)
19.5 | maximum air temperature | °C | ≥ +40
19.6 | minimum air temperature | °C | ≤ -30
technical specifications
19.7 | installation type |  | Outdoor instalation
19.8 | altitude above sea level | mtr. | ≤ 1000
19.9 | control regime |  | three-pole
operation
19.1 | nominal voltage | kw | 220
19.11 | maximum permitted voltage | kw | ≥245
19.12 | arc extinguishing area |  | SF6
19.13 | nominal frequency | Hz | 50
19.14 | industrial frequency testing voltage | kw | ≥460
19.15 | lightning impulse testing voltage | kw | ≥1050
19.16 | number of disconnecting spools | Pc. | 2 (Two)
19.17 | nominal current | A | ≥1250
19.18 | leakage way nominal distance | mm/kw | ≥25
19.19 | thermal stability current | ka | ≥40
19.2 | maximum dynamic stability current | ka | ≥100
19.21 | full time of switch-off | mk.Sec | ≤ 65
19.22 | length of short circuit | sec | ≥3
19.23 | nominal cycles of operations |  | O-0,3s-CO-3m-CO
19.24 | number of drive shafts |  | 1
19.25 | insulation material |  | porcelain
19.26 | distance between the phases | mm | 2800-3500
19.27 | supporting construction height | mm | 2400-2700
19.28 | driving voltage | v | 220 DC
19.29 | drive shafts' feeding voltage | v | 220 DC
19.3 | heater's feeding voltage | v | 220 AC
19.31 | number of interruptions on the pole |  | one
19.32 | circuit braker clips for AC-400/51 type wire | Pc. | 6
20 | Two earthening three-pole Disconnector with steel support structure and anchor fixing bolts and apparatus clamps
20.1 | standard |  | IEC 62271-102
or analogous
20.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
20.3 | maximum ice thickness | mm | ≥20
(forth zone)
20.4 | maximum wind speed | m/sec | ≥22
(second zone)
20.5 | maximum air temperature | °C | ≥ +40
20.6 | minimum air temperature | °C | ≤ -30
technical specifications
20.7 | installation type |  | Outdoor instalation
20.8 | altitude above sea level | mtr. | ≤ 1000
20.9 | control type |  | remote and local control
20.1 | drive shaft type |  | el. motor drive
20.11 | earthing blade with remote and local control |  | Two
20.12 | nominal voltage | kw | 220
20.13 | maximum operating voltage | kw | ≥ 245
20.14 | nominal frequency | Hz | 50
20.15 | nominal current | A | ≥ 1250
20.16 | thermal stability current | ka | ≥ 40
20.17 | maximum dynamic stability current | ka | ≥ 100
20.18 | switch on/off | sec | ≤ 10
20.19 | length of short circuit | sec | ≥1
20.2 | control regime |  | three-pole
20.21 | distance between the phases | mm | 4000
20.22 | supporting construction height | mm | 2400-2700
20.23 | driving voltage | v | 220 DC
20.24 | drive shafts' feeding voltage | v | 220 DC
20.25 | heater's feeding voltage | v | 220 AC
20.26 | insulation material |  | porcelain
20.27 | disconnector clips for AC-400/51 type wire | Pc. | 6
21 | One earthening three-pole disconnector with steel support structure, anchor, fixing bolts and apparatus clamps
21.1 | standard |  | IEC 62271-102
or analogous
21.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
21.3 | maximum ice thickness | mm | ≥20
(forth zone)
21.4 | maximum wind speed | m/sec | ≥22
(second zone)
21.5 | maximum air temperature | °C | ≥ +40
21.6 | minimum air temperature | °C | ≤ -30
technical specifications
21.7 | installation type |  | Outdoor instalation
21.8 | altitude above sea level | mtr. | ≤ 1000
21.9 | control type |  | remote and local control
21.1 | drive shaft type |  | el. motor drive
21.11 | earthing blade with remote and local control |  | one
21.12 | nominal voltage | kw | 220
21.13 | maximum permitted voltage | kw | ≥ 245
21.14 | nominal frequency | Hz | 50
21.15 | nominal current | A | ≥ 1250
21.16 | thermal stability current | ka | ≥ 40
21.17 | maximum dynamic stability current | ka | ≥ 100
21.18 | switch on/off | sec | ≤ 10
21.19 | length of short circuit | sec | ≥1
21.2 | control regime |  | three-pole
21.21 | distance between the phases | mm | 4000
21.22 | supporting construction height | mm | 2400-2700
21.23 | driving voltage | v | 220 DC
21.24 | drive shafts' feeding voltage | v | 220 DC
21.25 | heater's feeding voltage | v | 220 AC
21.26 | insulation material |  | porcelain
21.27 | disconnector clips for AC-400/51 type wire | Pc. | 6
22 | Surge arrestor with counter, with steel support structure, isolator and fixing bolts, with apparatus clamps.
22.1 | standard |  | IEC 60099-4
or analogous
22.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
22.3 | maximum ice thickness | mm | ≥20
(forth zone)
22.4 | maximum wind speed | m/sec | ≥22
(second zone)
22.5 | maximum air temperature | °C | ≥ +40
22.6 | minimum air temperature | °C | ≤ -30
technical specifications
22.7 | installation type |  | Outdoor instalation
22.8 | altitude above sea level | mtr. | ≤ 1000
22.9 | nominal voltageUr | kw | 192
22.1 | lastingly permitted voltage Uc | kw | ≥ 154
22.11 | nominal frequency | Hz | 50
voltage permitted values for period of time
22.12 | 10 sec | kw | ≥ 207
22.13 | 1 sec | kw | ≥ 221
22.14 | residual voltage 0,5 ka at the time of impulse current and a 30/70 mcsec wave front | kw | ≥ 380
22.15 | residual voltage Imax= 0,5 ka at the time of impulse current and a 8/20 mcsec wave front | kw | ≥ 438
22.16 | leakage way nominal distance | mm/kw | ≥ 25
22.17 | registrar with a mechanical face |  | Yes
22.18 | Surge arrestor clips for AC-400/51 type wire | Pc. | 6
22.19 | supporting construction height | mm | 3500-3700
23 | Supporting isolator with, steel structure, fixing nuts and bolts on steel structure, apparatus clamps
23.1 | standard |  | IEC 60273
or analogous
23.2 | typical test |  | upon delivery of the device
climate conditions
23.3 | maximum ice thickness | mm | ≥20
(forth zone)
23.4 | maximum wind speed | m/sec | ≥22
(second zone)
23.5 | maximum air temperature | °C | ≥ +40
23.6 | minimum air temperature | °C | ≤ -30
technical specifications
23.7 | insulator type |  | porcelain
23.8 | installation type |  | Outdoor instalation
23.9 | altitude above sea level | mtr. | ≤ 1000
23.1 | nominal voltage | kw | 220
23.11 | maximum permitted voltage | kw | ≥ 245
23.12 | minimum mechanical destructive power on bending | kn | ≥6
23.13 | minimum torque destructive moment | knm | ≥4
23.14 | lightning impulse testing voltage | kw | ≥1050
23.15 | industrial frequency testing voltage | kw | ≥460
23.16 | leakage way nominal length | mm | ≥ 6000
23.17 | leakage way nominal distance | mm/kw | ≥ 25
23.18 | supporting insulator clip for AC-400/51 type wire | Pc. | 1
23.19 | supporting construction height | mm | 3000-3200
24 | Gas insulated circuit braker (with 1 drive), with steel support structures, anchors, fixing bolts on steel structure, apparatus clamps
24.1 | standard |  | IEC 62271-100
or analogous
24.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
24.3 | maximum ice thickness | mm | ≥20
(forth zone)
24.4 | maximum wind speed | m/sec | ≥22
(second zone)
24.5 | maximum air temperature | °C | ≥ +40
24.6 | minimum air temperature | °C | ≤ -30
technical specifications
24.7 | installation type |  | Outdoor instalation
24.8 | altitude above sea level | mtr. | ≤ 1000
24.9 | control regime |  | three-pole
operation
24.1 | nominal voltage | kw | 110
24.11 | maximum permitted voltage | kw | ≥123
24.12 | arc extinguishing area |  | SF6
24.13 | nominal frequency | Hz | 50
24.14 | industrial frequency testing voltage | kw | ≥230
24.15 | lightning impulse testing voltage | kw | ≥550
24.16 | number of disconnecting spools | Pc. | 2 (Two)
24.17 | nominal current | A | ≥2000
24.18 | leakage way nominal distance | mm/kw | ≥25
24.19 | thermal stability current | ka | ≥20
24.2 | maximum dynamic stability current | ka | ≥50
24.21 | full time of switch-off | mk.Sec | ≤ 55
24.22 | length of short circuit | sec | ≥3
24.23 | nominal cycles of operations |  | O-0,3s-CO-3m-CO
24.24 | number of drive shafts |  | 1
24.25 | insulation material |  | porcelain
24.26 | distance between the phases | mm | 1700-2000
24.27 | supporting construction height | mm | 2400-2700
24.28 | driving voltage | v | 220 DC
24.29 | drive shafts' feeding voltage | v | 220 DC
24.3 | heater's feeding voltage | v | 220 AC
24.31 | number of interruptions on the pole |  | one
24.32 | circuit braker clips for AC-400/51 type wire | Pc. | 6
25 | Two earthening three-pole Disconnector with steel support structure and anchor fixing bolts and apparatus clamps
25.1 | standard |  | IEC 62271-102
or analogous
25.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
25.3 | maximum ice thickness | mm | ≥20
(forth zone)
25.4 | maximum wind speed | m/sec | ≥22
(second zone)
25.5 | maximum air temperature | °C | ≥ +40
25.6 | minimum air temperature | °C | ≤ -30
technical specifications
25.7 | installation type |  | Outdoor instalation
25.8 | altitude above sea level | mtr. | ≤ 1000
25.9 | control type |  | remote and local control
25.1 | drive shaft type |  | el. motor drive
25.11 | earthing blade with remote and local control |  | Two
25.12 | nominal voltage | kw | 110
25.13 | maximum operating voltage | kw | ≥ 123
25.14 | nominal frequency | Hz | 50
25.15 | nominal current | A | ≥ 1250
25.16 | thermal stability current | ka | ≥ 20
25.17 | maximum dynamic stability current | ka | ≥ 50
25.18 | switch on/off | sec | ≤ 10
25.19 | length of short circuit | sec | ≥1
25.2 | control regime |  | three-pole
25.21 | distance between the phases | mm | 2000
25.22 | supporting construction height | mm | 2400-2700
25.23 | driving voltage | v | 220 DC
25.24 | drive shafts' feeding voltage | v | 220 DC
25.25 | heater's feeding voltage | v | 220 AC
25.26 | insulation material |  | porcelain
25.27 | disconnector clips for AC-400/51 type wire | Pc. | 6
26 | One earthening three-pole disconnector with steel support structure, anchor, fixing bolts and apparatus clamps
26.1 | standard |  | IEC 62271-102
or analogous
26.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
26.3 | maximum ice thickness | mm | ≥20
(forth zone)
26.4 | maximum wind speed | m/sec | ≥22
(second zone)
26.5 | maximum air temperature | °C | ≥ +40
26.6 | minimum air temperature | °C | ≤ -30
technical specifications
26.7 | installation type |  | Outdoor instalation
26.8 | altitude above sea level | mtr. | ≤ 1000
26.9 | control type |  | remote and local control
26.1 | drive shaft type |  | el. motor drive
26.11 | earthing blade with remote and local control |  | one
26.12 | nominal voltage | kw | 110
26.13 | maximum operating voltage | kw | ≥ 123
26.14 | nominal frequency | Hz | 50
26.15 | nominal current | A | ≥ 1250
26.16 | thermal stability current | ka | ≥ 20
26.17 | maximum dynamic stability current | ka | ≥ 50
26.18 | switch on/off | sec | ≤ 10
26.19 | length of short circuit | sec | ≥1
26.2 | control regime |  | three-pole
26.21 | distance between the phases | mm | 2000
26.22 | supporting construction height | mm | 2400-2700
26.23 | driving voltage | v | 220 DC
26.24 | drive shafts' feeding voltage | v | 220 DC
26.25 | heater's feeding voltage | v | 220 AC
26.26 | insulation material |  | porcelain
26.27 | disconnector clips for AC-400/51 type wire | Pc. | 6
27 | Surge arrestor with counter, with steel support structure, isolator and fixing bolts, with apparatus clamps.
27.1 | standard |  | IEC 60099-4
or analogous
27.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
27.3 | maximum ice thickness | mm | ≥20
(forth zone)
27.4 | maximum wind speed | m/sec | ≥22
(second zone)
27.5 | maximum air temperature | °C | ≥ +40
27.6 | minimum air temperature | °C | ≤ -30
technical specifications
27.7 | installation type |  | Outdoor instalation
27.8 | altitude above sea level | mtr. | ≤ 1000
27.9 | nominal voltageUr | kw | 108
27.1 | lastingly permitted voltage Uc | kw | ≥ 86
27.11 | nominal frequency | Hz | 50
voltage permitted values for period of time
27.12 | 10 sec | kw | ≥ 117
27.13 | 1 sec | kw | ≥ 124
27.14 | residual voltage 0,5 ka at the time of impulse current and a 30/70 mcsec wave front | kw | ≥ 214
27.15 | residual voltage Imax= 0,5 ka at the time of impulse current and a 8/20 mcsec wave front | kw | ≥ 246
27.16 | leakage way nominal distance | mm/kw | ≥ 25
27.17 | registrar with a mechanical face |  | Yes
27.18 | Surge arrestor clips for AC-400/51 type wire | Pc. | 3
27.19 | supporting construction height | mm | 3600-3800
28 | Hybrid gas insulated circuit breaker with steel support structure, anchor, fixing bolts and apparatus clamps
28.1 | standard |  | IEC 62271-205
or analogous
28.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
28.3 | maximum ice thickness | mm | ≥20
(Forth zone)
28.4 | maximum wind speed | m/sec | ≥20
(second zone)
28.5 | maximum air temperature | °C | ≥ +40
28.6 | minimum air temperature | °C | ≤ -30
28.7 | Seismic Scale |  | ≥ 9
technical specifications
28.8 | installation type |  | outdoor instalation
28.9 | altitude above sea level | m | > 1000
28.1 | management regime |  | single-pole
management
28.11 | At the time emergency outage of circuit breaker, OHL side must not automatically earthing |  | yes
28.12 | nominal voltage | kv | 110
28.13 | maximum permitted voltage | kv | ≥123
28.14 | arc extinguishing area |  | SF6
28.15 | nominal frequency | Hz | 50
28.16 | industrial frequency testing voltage | kv | ≥230
28.17 | lightning impulse testing voltage | kv | ≥550
28.18 | number of disconnecting spools | pc. | 2 (two)
28.19 | nominal current | a | ≥1250
28.2 | leakage way nominal length | mm/kv | ≥25
28.21 | thermal stability current | ka | ≥20
28.22 | maximum dynamic stability current | ka | ≥50
28.23 | full time of switch-off | mk/sec | ≤ 55
28.24 | length of short circuit | sec | ≥3
28.25 | nominal cycles of operations |  | O-0,3s-CO-3m-CO
28.26 | Mechanical resource of operation |  | ≥10000
28.27 | number of drive shafts |  | 3
28.28 | insulation material |  | porcelain
28.29 | supporting construction height | mm | 2400-2700
28.3 | driving voltage | v | 220 DC
28.31 | drive shafts' feeding voltage | v | 220 DC
28.32 | heater's feeding voltage | v | 220 AC
28.33 | circuit breaker clips for AC-400/51 type wire | Pc. | 6
The hybrid gas-insulated breaker tank should not be welded and in the tank should be
28.34 | disconnector with one earthing blade |  | Please see chart
28,34,1 | standard |  | IEC 62271-102
or analogous
28,34,2 | nominal current | a | ≥1250
28,34,3 | length of short circuit | sec | ≥3
28,34,4 | industrial frequency testing voltage | kv | ≥230
28,34,5 | lightning impulse testing voltage | kv | ≥550
28,34,6 | driving voltage | v | 220 DC
28,34,7 | drive shafts' feeding voltage | v | 220 DC
28,34,8 | heater's feeding voltage | v | 220 AC
28.35 | current transformer |  | Please see chart
28,35,1 | standard |  | IEC 61869
or analogous
28,35,2 | nominal primary current | a | 600/300
28,35,3 | nominal secondary current | a | 5
28,35,4 | number of secondary rolls |  | 4
precision classes and capacities of the secondary rolls
28,35,5 | roll-1, coefficient 600/5, precision class and capacity =0,5S – 30VA |  | roll is sealed
28,35,6 | roll-1, coefficients 300/5, precision class and capacity 0,5S – 30VA |  | roll is sealed
28,35,7 | roll-2, 3 and 4 coefficients 600/5, precision class and capacity 10P20 - 50VA
28,35,8 | roll-2, 3 and 4 coefficients 300/5, precision class and capacity 10P20 - 50VA
28,35,9 | Change of the coefficients of the current transformers should be possible from the secondary roll |  | Yes
28.36 | voltage transformers |  | Please see chart
28,36,1 | standard |  | IEC 61869
or analogous
28,36,2 | roll -1, registry, voltage, v -100/√3 precision class and capacity , VA - 0,5/10 |  | roll is sealed
28,36,3 | roll - 2, reley protection, voltage
V -100/√3 precision class and
capacity VA - 3P/50
29 | Hybrid gas insulated circuit breaker with steel support structure, anchor, fixing bolts and apparatus clamps
29.1 | standard |  | IEC 62271-205
or analogous
29.2 | submission of the test protocols |  | upon delivery of the device
climate conditions
29.3 | maximum ice thickness | mm | ≥20
(forth zone)
29.4 | maximum wind speed | m/sec | ≥20
(second zone)
29.5 | maximum air temperature | °C | ≥ +40
29.6 | minimum air temperature | °C | ≤ -30
29.7 | Seismic Scale |  | ≥ 9
technical specifications
29.8 | installation type |  | outdoor instalation
29.9 | altitude above sea level | m | >1000
29.1 | management regime |  | single-pole
management
29.11 | At the time emergency outage of circuit breaker, OHL side must not automatically earthing |  | yes
29.12 | nominal voltage | kv | 110
29.13 | maximum permitted voltage | kv | ≥123
29.14 | arc extinguishing area |  | SF6
29.15 | nominal frequency | Hz | 50
29.16 | industrial frequency testing voltage | kv | ≥230
29.17 | lightning impulse testing voltage | kv | ≥550
29.18 | number of disconnecting spools | Pc. | 2 (two)
29.19 | nominal current | a | ≥1250
29.2 | leakage way nominal length | mm/kv | ≥25
29.21 | thermal stability current | ka | ≥20
29.22 | maximum dynamic stability current | ka | ≥50
29.23 | full time of switch-off | mk/sec | ≤ 55
29.24 | length of short circuit | sec | ≥3
29.25 | nominal cycles of operations |  | O-0,3s-CO-3m-CO
29.26 | Mechanical resource of operation |  | ≥10000
29.27 | number of drive shafts |  | 3
29.28 | insulation material |  | porcelain
29.29 | supporting construction height | mm | 2400-2700
29.3 | driving voltage | v | 220 DC
29.31 | drive shafts' feeding voltage | v | 220 DC
29.32 | heater's feeding voltage | v | 220 AC
29.33 | circuit breaker clips for AC-400/51 type wire | Pc. | 6
The hybrid gas-insulated breaker tank should not be welded and in the tank should be
29.34 | disconnector with one earthing blade |  | Please see chart
29,34,1 | standard |  | IEC 62271-102
or analogous
29,34,2 | nominal current | a | ≥1250
29,34,3 | length of short circuit | sec | ≥3
29,34,4 | industrial frequency testing voltage | kv | ≥230
29,34,5 | lightning impulse testing voltage | kv | ≥550
29,34,6 | driving voltage | v | 220 DC
29,34,7 | drive shafts' feeding voltage | v | 220 DC
29,34,8 | heater's feeding voltage | v | 220 AC
29.35 | current transformer |  | Please see chart
29,35,1 | standard |  | IEC 61869
or analogous
29,35,2 | nominal primary current | a | 800/400
29,35,3 | nominal secondary current | a | 1
29,35,4 | number of secondary rolls |  | 4
precision classes and capacities of the secondary rolls
29,35,5 | roll-1, coefficient 800/1, precision class and capacity =0,5S – 10VA |  | roll is sealed
29,35,6 | roll-1, coefficients 400/1, precision class and capacity 0,5S – 10VA |  | roll is sealed
29,35,7 | roll-2, 3 and 4 coefficients 800/1, precision class and capacity 10P20 - 50VA
29,35,8 | roll-2, 3 and 4 coefficients 400/1, precision class and capacity 10P20 - 50VA
29,35,9 | Change of the coefficients of the current transformers should be possible from the secondary roll |  | Yes
29.36 | voltage transformers |  | Please see chart
29,36,1 | standard |  | IEC 61869
or analogous
29,36,2 | roll -1, registry, voltage, v -100/√3 precision class and capacity , VA - 0,5/10 |  | roll is sealed
29,36,3 | roll - 2, reley protection, voltage
v -100/√3 precision class and
capacity VA - 3P/50
30 | one drive shaft gas-insulated switchgear th metal construction with two earthing blades. anchor screws and bolts, apparatus clips
30,1 | standard |  | IEC 62271-100
or analogous
climate conditions
30,2 | maximum ice thickness | mm | ≥15
30,3 | maximum wind speed | m/s | ≥37
30,4 | maximum air temperature | °C | ≥ +40
30,5 | minimum air temperature | °C | ≤ -25
technical specifications
30,6 | installation type |  | outdoor instalation
30,7 | altitude above sea level | mtr. | ≤ 1000
30.8 | control regime |  | three-pole operation
30,9 | nominal voltage | kw | 110
30,10 | maximum permitted voltage | kw | ≥123
30,11 | arc extinguishing area |  | SF6
30,12 | nominal frequency | Hz | 50
30,13 | industrial frequency testing voltage | kw | ≥230
30,14 | lightning impulse testing voltage | kw | ≥550
30,15 | number of disconnecting spools | pc. | 2 (two)
30,16 | nominal current | A | ≥1250
30,17 | leakage way nominal length | mm/kv | ≥25
30,18 | thermal stability current | ka | ≥31,5
30,19 | maximum dynamic stability current | ka | ≥78
30,20 | full time of switch-off | mk.wm | ≤ 55
30,21 | length of short circuit | sec | ≥3
30,22 | nominal cycles of operations |  | O-0,3s-CO-3m-CO
30,23 | number of drive shafts |  | 1
30,24 | insulation material |  | porcelain
30,25 | distance between the phases | mm | 1700-2000
30,26 | supporting construction height | mm | 2400-2700
30,27 | driving voltage | v | 220 DC
30,28 | drive shafts' feeding voltage | v | 220 DC
30,29 | heater's feeding voltage | v | 220 AC
30,30 | number of interruptions on the pole |  | one
30,31 | switch clips for AC-400/51 type wire | pc. | 6
31 | Diagonal Disconnector, with steel support structures and anchor, fixin bolts, with apparatus clamps.
31,1 | standard |  | IEC 62271-102
or analogous
climate conditions
31,2 | maximum ice thickness | mm | ≥15
31,3 | maximum wind speed | m/s | ≥37
31,4 | maximum air temperature | °C | ≥ +40
31,5 | minimum air temperature | °C | ≤ -25
technical specifications
31,6 | installation type |  | outdoor instalation
31,7 | altitude above sea level | mtr. | ≤ 1000
31,8 | control type |  | remote and local control
31,9 | drive shaft type |  | el. motor drive
31,10 | earthing blade |  | without
31,11 | arrangement |  | Diagonal
31,12 | nominal voltage | kw | 110
31,13 | maximum operating voltage | kw | ≥ 123
31,14 | nominal frequency | Hz | 50
31,15 | nominal current | A | ≥ 1250
31,16 | thermal stability current | ka | ≥31,5
31,17 | maximum dynamic stability current | ka | ≥78
31,18 | switch on/off | sec | ≤ 10
31,19 | length of short circuit | sec | ≥1
31,20 | control regime |  | three-pole
31,21 | distance between the phases | mm | 2000
31,22 | supporting construction height | mm | 2400-2700
31,23 | driving voltage | v | 220 DC
31,24 | drive shafts' feeding voltage | v | 220 DC
31,25 | heater's feeding voltage | v | 220 AC
31,26 | insulation material |  | porcelain
31,27 | disconnector clips for AC-400/51 type wire | pc. | 6
32 | three-pole disconnecter with one earthing blade, with metal construction. anchor screws and nuts and apparatus clips
32,1 | standard |  | IEC 62271-102
or analogous
climate conditions
32,2 | maximum ice thickness | mm | ≥15
32,3 | maximum wind speed | m/s | ≥37
32,4 | maximum air temperature | °C | ≥ +40
32,5 | minimum air temperature | °C | ≤ -25
technical specifications
32,6 | installation type |  | outdoor instalation
32,7 | altitude above sea level | mtr. | ≤ 1000
32,8 | control type |  | remote and local control
32,9 | drive shaft type |  | el. motor drive
32,10 | earthing blade with remote and local control |  | one
32,11 | nominal voltage | kw | 110
32,12 | maximum operating voltage | kw | ≥ 123
32,13 | nominal frequency | Hz | 50
32,14 | nominal current | A | ≥ 1250
32,15 | thermal stability current | ka | ≥31,5
32,16 | maximum dynamic stability current | ka | ≥78
32,17 | switch on/off | sec | ≤ 10
32,18 | length of short circuit | sec | ≥1
32,19 | control regime |  | three-pole
32,20 | distance between the phases | mm | 2000
32,21 | supporting construction height | mm | 2400-2700
32,22 | driving voltage | v | 220 DC
32,23 | drive shafts' feeding voltage | v | 220 DC
32,24 | heater's feeding voltage | v | 220 AC
32,25 | insulation material |  | porcelain
32,26 | disconnector clips for AC-400/51 type wire | pc. | 6
33 | Voltage increase restrictor with a metal construction, anchor screws and bolts, apparatus clips and registrator - with insulators and screws-bolts to be fitted to the metal construction
33,1 | standard |  | IEC 60099-4
or analogous
climate conditions
33,2 | maximum ice thickness | mm | ≥15
33,3 | maximum wind speed | m/w | ≥37
33,4 | maximum air temperature | °C | ≥ +40
33,5 | minimum air temperature | °C | ≤ -25
technical specifications
33,6 | installation type |  | outdoor instalation
33,7 | altitude above sea level | mtr. | ≤ 1000
33,8 | nominal voltageUr | kw | 108
33,9 | lastingly permitted voltage Uc | kw | ≥ 86
33,10 | nominal frequency | Hz | 50
voltage permitted values for period of time
33,11 | 10 sec | kw | ≥ 117
33,12 | 1 sec | kw | ≥ 124
33,13 | residual voltage 0,5 ka at the time of impulse current and a 30/70 mcsec wave front | kw | ≥ 214
33,14 | residual voltage Imax= 0,5 ka at the time of impulse current and a 8/20 mcsec wave front | kw | ≥ 246
33,15 | leakage way nominal length | mm/kw | ≥ 25
33,16 | registrar with a mechanical face |  | yes
33,17 | Voltage increase restrictor ძclips for AC-400/51 type wire | pc. | 3
33,18 | supporting construction height | mm | 2400-2500
34 | Support insulation with a metal construction, anchor screws and bolts, apparatus clips and registrator - with insulators and screws-bolts to be fitted to the metal construction
34,1 | standard |  | IEC 60273
or analogous
climate conditions
34,2 | maximum ice thickness | mm | ≥15
34,3 | maximum wind speed | m/w | ≥37
34,4 | maximum air temperature | °C | ≥ +40
34,5 | minimum air temperature | °C | ≤ -25
technical specifications
34,6 | insulator type |  | porcelain
34,7 | installation type |  | outdoor instalation
34,8 | altitude above sea level | mtr. | ≤ 1000
34,9 | nominal voltage | kw | 110
34,10 | maximum permitted voltage | kw | ≥ 123
34,11 | minimum mechanical destructive power on bending | kn | ≥6
34,12 | minimum torque destructive moment | knm | ≥3
34,13 | lightning impulse testing voltage | kw | ≥550
34,14 | industrial frequency testing voltage | kw | ≥230
34,15 | leakage way nominal length | mm | ≥ 2900
34,16 | leakage way nominal length | mm/kv | ≥ 25
34,17 | supporting insulator clip for AC-400/51 type wire | pc. | 3
34,18 | supporting construction height | mm | 2400-2500