## ADGO33
Annex #1.5 _ Bill of Quantities
State Procurement of Construction Works of 33km segment of “Adigeni-Goderdzi” Main Gas Pipeline (Dn300)
Ref.: ADGO33-GS03-CM-BOQ-0001-GEO-A01
# | Activity | Unit | Quantity | Unit Price excluding VAT | Total Price excluding VAT
1 | ROW Preparation
1.1 | Prepation of pipeline ROW and Topsoil stripping/storage along the pipeline ROW | m | 32928 |  | 0
1,2 | Prepation of side slope in pipeline ROW | m | 564 |  | 0
2 | Transportation of Pipes and other Fittings to the Construction Site
2.1 | Transportation and stringing of DN300 pipes | m | 33262 |  | 0
2.2 | Transportation of DN200 coated pipes | m | 12 |  | 0
2.3 | Transportation of DN100 coated pipes | m | 204 |  | 0
2.4 | Transportation of DN80 coated pipes | m | 36 |  | 0
2.5 | Transportation of bends, valves and fittings | pcs | 347 |  | 0
3 | Welding
3.1 | Welding of DN300 pipes, corresponding bends and fittings in the pipeline ROW | m | 33262 |  | 0
4 | Inspection of Welded Joints
4.1 | X-ray of DN300 welded joints | m | 33262 |  | 0
4.2 | X-ray of DN300 valve unit | unit | 2 |  | 0
4.3 | X-ray of DN100 valve unit and DN100 branch | unit | 1 |  | 0
4.4 | X-ray of DN800 valve unit and DN80 branch | unit | 2 |  | 0
5 | Coating Works
5.1 | Sandblasting of DN300 welded joints and coating with anticorrosion thermal sleeves | m | 33262 |  | 0
5.2 | Sandblasting of DN300 valve unit welded joints and insulation according to pipe coating | unit | 2 |  | 0
5.3 | Sandblasting of DN100 valve unit and DN100 welded joints and insulation according to pipe coating | unit | 1 |  | 0
5.4 | Sandblasting of DN80 valve unit and DN80 welded joints and insulation according to pipe coating | unit | 2 |  | 0
5.5 | Wrapping of DN300 pipeline with "Rockshield" | მ | 33262 |  | 0
6 | Trenching
6.1 | Trenching for DN300 pipeline section | m | 33262 |  | 0
7 | Pipe Lowering and Backfilling
7.1 | Lowering of DN300 coated pipe | m | 33262 |  | 0
7.2 | Backfilling of DN300 pipe trench | m | 33262 |  | 0
8 | Crossing of river and ravines
Crossing of the ravine on kp 21+975
8.1 | Arrangement of concrete slabs (6X2X0.2) | pcs | 10 |  | 0
8.2 | Arrangement of concrete slabs (5X2X0.2) | pcs | 10 |  | 0
8.3 | Arrangement of concrete blocks (2.1X1X0.6) | pcs | 18 |  | 0
Crossing of the ravine on kp 23+530
8.4 | Arrangement of concrete slabs (6X2X0.2) | pcs | 12 |  | 0
8.5 | Arrangement of concrete blocks (2.1X1X0.6) | pcs | 22 |  | 0
Crossing of the ravine on kp 25+010
8.6 | Arrangement of concrete slabs (6X2X0.2) | pcs | 12 |  | 0
8.7 | Arrangement of concrete blocks (2.1X1X0.6) | pcs | 22 |  | 0
Crossing of the ravine on kp 25+010
8.8 | Arrangement of concrete slabs (6X2X0.2) | pcs | 12 |  | 0
8.9 | Arrangement of concrete blocks (2.1X1X0.6) | pcs | 22 |  | 0
Crossing of the ravine on kp 25+010
8.10 | Arrangementof concrete slabs (6X2X0.2) | pcs | 10 |  | 0
8.11 | Arrangement of concrete blocks (2.1X1X0.6) | pcs | 18 |  | 0
Crossing of the river on kp 26+430
8.12 | Arrangement of concrete slabs (6X2X0.2) | pcs | 5 |  | 0
8.13 | Arrangement of concrete blocks (2.1X1X0.6) | pcs | 26 |  | 0
9 | Concrete Works
9.1 | Reinforced concreting (6 cm) of DN300 pipes with - B25 concrete and wrapping rockshield on welded joints | m | 216 |  | 0
9.2 | Arrangement of Concrete Slabs Above the Pipeline (1X0.5X0.15) | pcs | 3510 |  | 0
10 | Pipe Cleaning and Hydrotesting
10.1 | DN300 pipe cleaning with brush and magnet pig, equipped with caliper plate *(See Note) | m | 33262 |  | 0
10.2 | DN300 pipe pneumatic testing on integrity at P=5.94 Mpa for 12 hours and on hermeticity at P=5,4 Mpa for 12 hours | m | 33262 |  | 0
10.3 | Pneumatic Pretesting of DN300 Valve station according to drawings ADGO33-GS03-PL-SCM-00002 and ADGO33-GS03-PL-SCM-00003 | unit | 2 |  | 0
10.4 | Pneumatic Pretesting of DN100 Valve station according to drawings ADGO33-GS03-PL-SCM-00002 and ADGO33-GS03-PL-SCM-00003 parameters | unit | 1 |  | 0
10.5 | Pneumatic Pretesting of DN100 Valve station according to drawings ADGO33-GS03-PL-SCM-00002 and ADGO33-GS03-PL-SCM-00003 parameters | unit | 2 |  | 0
11 | Valve Stations
11.1 | Arrangement of DN300 valve unit according to drawing | pcs | 2 |  | 0
11.2 | Arrangement of DN100 valve unit according to drawing | pcs | 1 |  | 0
11.3 | Arrangement of DN80 valve unit according to drawing | pcs | 2 |  | 0
11.4 | Arrangement of DN300 valve unit area according to drawing | pcs | 2 |  | 0
11.5 | Arrangement of DN100 valve unit area according to drawing | pcs | 1 |  | 0
11.6 | Arrangement of DN80 valve unit area according to drawing | pcs | 2 |  | 0
11.7 | Arrangement of gas uptake impulse system per drawings for DN300 valve unit | pcs | 2 |  | 0
11.8 | Arrangement of gas uptake impulse device per drawings for DN100 valve unit | pcs | 1 |  | 0
11.9 | Arrangement of gas uptake impulse nozzle per drawings for DN80 valve unit | pcs | 2 |  | 0
12 | Antierossion works
12.1 | Arrengement of water diversion berms in the pipeline ROW | pcs | 306 |  | 0
12.2 | Arangement of trench breakers | pcs | 518 |  | 0
13 | Electrochemical Protection
13.1 | Installation of УКЗH-0,23-1,2-48-1-У1 type cathodic protection station with automatic regulation and GSM modem | pcs | 2 |  | 0
13.2 | Arrangement of base for cathodic protection station using reinforced concrete | pcs | 2 |  | 0
13.3 | Arrangement of fencing for cathodic protection station per typical drawing | pcs | 2 |  | 0
13.4 | Arrangement of grounding for cathodic protection station per typical drawing | pcs | 2 |  | 0
13.5 | Arrangement of anode grounding per typical drawing | unit | 2 |  | 0
13.6 | Installation of one ВВГ 2×25-660 cable underground (from CP station to anode bed post) | m | 543 |  | 0
13.7 | Installation of one ВВГ 2×25-660 cable underground (from CP station to pipeline) | m | 46 |  | 0
13.8 | Installation of one ВВГ 2×6-660 cable underground (from CP post to pipe on four point, in distance of 56m and 6m from drainage point) | m | 232 |  | 0
13.9 | Installation of combined areal marker and control-measurement units (AM/CP) with as per drawing | pcs | 34 |  | 0
13.10 | Installation of control-measurement units (CP) as per drawing | pcs | 9 |  | 0
13.11 | Equipping control measurement points with permanent (ЭНЕС-1) comparison electrode according to drawing | pcs | 43 |  | 0
13.12 | Installation of ВВГ 1×16-660 one cable in the trench of anode grounding | m | 210 |  | 0
13.13 | Installation of signal tape in the trench at the depth of 0,75 m | m | 1031 |  | 0
14 | Other Works
14.1 | Installation of signal tape along the pipeline in the trench | m | 33262 |  | 0
14.2 | Installation of pipeline marker posts (MP,AM) according to drawing | pcs | 226 |  | 0
14.3 | Installation of DN300 insolation joint (joint to be welded) | pcs | 2 |  | 0
14.4 | Installation of DN100 insolation joint (joint to be welded) | pcs | 1 |  | 0
14.5 | Installation of DN80 insolation joint (joint to be welded) | pcs | 2 |  | 0
14.6 | Arrangement of DN100 casing pipe (3pcsX8meters) for optical cable according to drawing | m | 24 |  | 0
14.7 | Reinstatement of the construction area to initial condition | m | 33262 |  | 0
|  |  | Total price excluding VAT |  | 0
|  |  | Total price including VAT |  | 0
*Note: 1. Presented cost estimate shall consider cost of all those materials and devices that are required by the construction design and wich are not provided by Purchaser.
2. Cost estimate should considers cost of cold bending of pipes.
3. Following the completion of works in 10.1 if a caliper plate has identified defects, the contractor shall furnish and run a caliper/geometry inspection tool (intelligent PIG) with instrumentation having defect location identification capabilities, at own expenses.
3. The address of the pipeyard: see provaided material list
4. Following the completion of works in 7.1 and 7.2 shall be performed with strict compliance of Scope of Work document